TITLE 35:  ENVIRONMENTAL PROTECTION

SUBTITLE C:  WATER POLLUTION

CHAPTER II:  ENVIRONMENTAL PROTECTION AGENCY

PART 374

DESIGN CRITERIA OF PRESSURE SEWER SYSTEMS

SUBPART A:  PERMITS

Section

374.101   Introduction

374.102   Conventional System Preference

374.103   System Pressure Maintenance

374.104   Sludge Disposal

374.105   Sludge Disposal (Renumbered)

374.106   Pressure System Failure (Repealed)

SUBPART B:  DESIGN CRITERIA

Section

374.201   Duplex Pumps

374.202   Minimum Size

374.203   Valves

374.204   Non-corrosive Equipment

374.205   Influent Pumping

374.206   Pump Vaults

374.207   Marked Sewer Lines

374.208   Alarm Systems

AUTHORITY:  Authorized by and implementing Section 13(a)(3) of the

Environmental Protection Act [415 ILCS 5/13(a)(3)].

SOURCE:  Filed with the Secretary of State December 20, 1977, effective

December 20, 1977; codified at 6 Ill. Reg. 13019, effective October 12,

1982; amended at 21 Ill. Reg. 12439, effective August 28, 1997.

SUBPART A:  PERMITS

<BSection 374.101  Introduction>>

These design criteria are to be used by the Illinois Environmental

Protection Agency in reviewing 35 Ill. Adm. Code 309, Subpart B permit

applications for pressure sewer systems including grinder pump systems and

septic tank effluent pumping (STEP) systems.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)

<BSection 374.102  Conventional System Preference>>

If possible, the development proposed shall be served by a conventional

sewer system.  A conventional sewer system is defined as gravity sewers or

a conventionally designed pumping station.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)

<BSection 374.103  System Pressure Maintenance>>

The owner or operator of a pressure sewer system shall provide a method of

inspection or authorization to assure that users of the system maintain the

original design operating pressures of the system when repairing, modifying

or replacing any of the pumping equipment on the user's premises.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)

<BSection 374.104  Sludge Disposal>>

Permits for STEP systems shall not be issued unless the applicant provides

satisfactory evidence that adequate facilities are available for the

pumping and disposal of septic tank sludge.

(Source:  Section 374.104 repealed and new Section 374.104 renumbered

from Section 374.105 at 21 Ill. Reg.12439, effective August 28,

1997)

<BSection 374.105  Sludge Disposal (Renumbered)>>

(Source:  Section 374.105 renumbered to Section 374.104 at 21 Ill.

Reg. 12439, effective August 28, 1997)

<BSection 374.106  Pressure System Failure (Repealed)>>

(Source:  Repealed at 21 Ill. Reg. 12439, effective August 28, 1997)

SUBPART B:  DESIGN CRITERIA

<BSection 374.201  Duplex Pumps>>

If grinder pumps are serving more than one building, duplex pumping units

shall be required.  If the pumps are to be installed for individual

buildings, a single pumping unit may be used.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)

<BSection 374.202  Minimum Size>>

The grinder pump "wet well" should have a minimum size of 150 gallons.

<BSection 374.203  Valves>>

Valve arrangements and connection shall be made so as to allow quick

removal and replacement of equipment for maintenance purposes.

<BSection 374.204  Non-corrosive Equipment>>

Non-corrosive or corrosion-resistant equipment shall be specified for STEP

systems.

<BSection 374.205  Influent Pumping>>

In the STEP systems, pump well influent piping should enter at the bottom

of the well to prevent cascading of septic effluent in order to minimize

both odor and corrosion.

<BSection 374.206  Pump Vaults>>

All pump vaults shall be equipped with locking covers.

<BSection 374.207  Marked Sewer Lines>>

Where polyvinyl chloride (PVC) pressure mains are to be installed in the

vicinity of similar water supply lines, the sewer line should be clearly

marked to prevent possible future cross-connections.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)

<BSection 374.208  Alarm Systems>>

An alarm system shall be provided in the home where grinder units are

installed in the basement to alert the home owner in case of pump

malfunction.  A visual alarm system shall be provided for those pumping

units installed in a separate pumping vault outside of the home.

(Source:  Amended at 21 Ill. Reg. 12439, effective August 28, 1997)