## Sheet1
Table: List of Existing and New Simple Cycle, and New Combined Cycle Units
Combined Cycle Units are Highlighted |  |  |  |  | F:utility\peakersEGU\sheet 2\10-31-2000\v gupta
S. | ID # | Company Name | Street Address | Location | County | EGU Site | Ozone |  | Permit | Date | Date | Oper. Permit |  | Turbine | No. of |  |  | Alternative | Existing | Turbine | MW | Turbine | Duct Burner |  | Load | NOx limit |  | N. Gas Limit, mmcf |  | F. Oil Limit | Hrs of Operation Limit / yr |  | Nox Rate | NOx Rate | NOx Emissions | Startup | Acid Rain | NSPS Monitoring | Other Monitoring |  | Review/
No. | [5 empty] | Existing/ | Attainment | Permit | Type | Applic. | Permit | Expiration** | Permit Action | Unit | Identical | Turbine | Turbine | Turbine | Under | NOx | Capacity/ | Heat Input | H.Input |  | Type | per turbine | All Turbines @Site | per turbine | All Turbines | All Turbines @Site | per | All Turbines | ppm | lb per mmBtu | During Startup | Time | Monitoring | 40CFR60.334(a) | (daily, annual etc.) |  | Const./Oper.
[6 empty] | New | Yes/No | Number | C/O | Rec'd | Issued | Date | Status | Type | Turbines | Manufacturer | Model No. | Proposal | Subpart W | Control | Turbine | mmBtu/hr | mmBtu/hr | Fuel Used |  | lb per hour | tpy | per hr | @Site/yr | mmGal./Yr. | turbine | @Site |  |  | lb/hr | min | 40CFR75*² | and Others sections | /Recordkeeping | Applicable Rule | Status
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
1 | 021814AAG | Dom. Energy-Lincoln Generation | Route 104 | Kincaid | Christian | Existing | Yes | 00020011 | C | 2/3/00 |  |  | Add. Info Ltr 3/6/00 | SCT | 4 | GE | 7FA Frame |  | No | DLN | 172 | 1972 |  | N.Gas | Peaking | [7 empty] | 9 | 0.036 | [5 empty] | Major-PSD | Under Review
2 | 025803AAD | Aquila Energy/MEP Flora Power | Route 2, Box 89a | Harter/Flora | Clay | New | Yes | 00050050 | C | 2000-05-08 |  |  | Review Pending | SCT | 6 | GE | 7EA Frame |  | No | DLN | 94.5 | 1001.7 |  | N.Gas | Peaking | 60 | 245 |  | 8475 |  |  |  | 9-15 | 0.036-0.060 | [5 empty] | NSPS | Under Review
3 | 025804AAC | Entergy Power-Flora Peaking Stn | To Be Determined | Flora | Clay | New | Yes | 00030053 | C | 2000-03-16 |  |  | Public Notice | SCT | 4 | GE | 7EA Frame |  | No | DLN | 73 | 1024 |  | N.Gas | Peaking | 55 | 212 | [5 empty] | 9-15 | 0.036-0.060 | [5 empty] | NSPS | Under Review
4 | 025804AAC | Entergy Power-Flora Peaking Stn | To Be Determined | Flora | Clay | New | Yes | 00030053 | C | 2000-03-16 |  |  | Public Notice | SCT | 2 | GE | 7FA Frame |  | No | DLN | 148 | 1747 |  | N.Gas | Peaking | 99 | 212 | [5 empty] | 9 | 0.018 | [5 empty] | NSPS | Under Review
5 | 031600AMI | Midwest Generation | 1111 W Cermak Rd | Chicago | Cook | Existing | No | 95090081 | Title V | 1995-09-07 |  |  | Review Pending | SCT | 8 | Worthington | GG4 |  | Yes | None | 33 | 558 |  | JP-4, N.G. | Peaking | [7 empty] | 110(JP-4), 70 (g) | 0.44 (o) 0.28(g) | [5 empty] | None | Existing Peaker
6 | 031600GGV | People's Energy/Calumet Power | 3200 E 98th St | Chicago | Cook | New | No | 99100023 | C | 1999-10-07 | 2000-03-24 |  | Permitted | SCT | 2 | ABB | 11N2 |  | No | WI | 133 | 1500 |  | N.Gas Only | Peaking | 151.2 | 233 | 3.25 | 5002 |  |  |  | 25 | 0.1 |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Pending
7 | 031600GHA | Calumet Energy Team LLC | 10301 S Doty Ave | Chicago | Cook | New | No | 99110107 | C | 1999-11-24 | 2000-05-19 |  | Permitted | SCT | 2 | ABB | 11N2 |  | No | DLN or WI | 152.5 | 1604 |  | N.Gas/Oil | Peaking | 170 (g) 317 (o) | 240 | 1.6 | 4870 | 8 |  |  | 25-g/42-oil | 0.10(g)-0.168(o) |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Initiated
8 | 031801AAI | Duke Energy Chicago Hts | 1600 Feet West Of Cottage Grove Rd | Chicago Hts | Cook | New | No | 00040068 | C | 2000-04-24 |  |  | Review Pending | CCT | 2 | GE | 7FA Frame |  | No | SCR | 310 | 4232 |  | N.Gas | Base | [7 empty] | 3.5 | 0.014 |  |  |  |  | fuel use,Btu,N, reagent use, oper. Hrs | Major | Under Review
9 | 041806AAC | Ener Star- Montana Stn | Rural | Newman | Douglas | New | Yes | 00060075 | C | 2000-06-22 |  |  | Review Pending | SCT | 2 | GE | 7FA Frame |  | No | DLN | 161 | 1640 |  | N.Gas | Peaking | [7 empty] | 9 | 0.036 | [5 empty] | NSPS | Under Review
10 | 041806AAC | Ener Star- Montana Stn | Rural | Newman | Douglas | New | Yes | 00060075 | C | 2000-06-22 |  |  | Review Pending | SCT | 1 | GE | 7FA Frame |  | No | DLN | 40 | 400 |  | N.Gas | Peaking | [7 empty] | 25 | 0.1 | [5 empty] | NSPS | Under Review
11 | 043090ADB | Standard Energy Venture, LLC | McChesney Rd and Fabyan Pkwy | W.Chicago | Du Page | New | No | 99120001 | C | 1999-12-01 |  |  | Draft Permit | SCT*** | 16 | Pratt & Whittney | FT8 "Twin Packs"Aero |  | No | SCN ?? (DLN??)/WI(o) | 50 | 554.8 | 430?? | N.Gas/Oil | Base/Peaking | 54(g) 194(o) | 732 |  |  |  | 2500(Total);500 (o) | 20000 | 12 (annual) 15 (hourly) | 0.06 (g), 0.17 (o) | 1.68 tpy Startup/shut down (all units total) |  | Yes | Yes | fuel usage,Btu, water usage, oper. Hrs | PSD/BACT | Under Review
12 | 043407AAF | Reliant Energy/Reliant DuPage Cty LP | Eola Rd @ Ferry Rd | Aurora | Du Page | New | No | 99110018 | C | 1999-10-29 | 2000-05-09 |  | Permitted | SCT | 4 | GE | 7FA Frame |  | No | DLN | 170 | 1885 |  | N.Gas Only | Peaking | 105 | 247 |  | 9878 |  |  |  | 9 | 0.036 |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, oper. Hrs | NSPS | Const. Initiated
13 | 043407AAF | Reliant Energy/Reliant DuPage Cty LP | Eola Rd @ Ferry Rd | Aurora | Du Page | New | No | 99110018 | C | 1999-10-29 | 2000-05-09 |  | Permitted | SCT | 6 | GE (Stewart & Stevenson) | LM6000 PC |  | No | WI | 45 | 444 |  | N.Gas Only | Peaking | 41 | 247 |  | 9878 |  |  |  | 25 | 0.1 |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Initiated
14 | 043412AAH | Grand Prairie Energy, LLC/ABB | Old Bartlett Quarry | Bartlett | Du Page | New | No | 99090051 | C | 1999-09-16 | 2000-09-05 |  | Permitted | CCT | 2 |  |  |  | No | DLN(g), WI(o), SCR (HRSG) | 250 | 1868 |  | N.G./Oil | Base | 24.5(g) 67.6 (o) | 213 |  |  |  | 480(o) |  | 4.5 (g), 10.5 (o) | 0.017 (g), 0.043 (o) |  |  | Yes |  | fuel usage, water/fuel ratio, SCR reagent, fuel Btu | PSD/BACT | Const. Pending
15 | 051030AAD | Spectrum Energy/C.I. C.S.Power | 1 mile NE of city of St. Peters | St. Peters | Fayette | New | Yes | 99100013 | C | 1999-10-04 | 2000-02-01 |  | Permitted | SCT | 1 | GE | LM6000 Aero |  | No | WI | 45 | 420 |  | N.Gas Only | Peaking | 43 | 85.9 |  | 1700 |  | 4000 |  | 25 | 0.1 |  | 20 | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Pending
16 | 051808AAK | Cent.Ill. S C Pow./ Spectrum | State Route 4 | St. Elmo | Fayette | New | Yes | 99060052 | C | 1999-06-16 | 1999-09-07 |  | Permitted | SCT | 1 | GE | LM6000 Aero |  | No | WI | 45 | 420 |  | N.Gas Only | Peaking | 43 | 85.9 |  | 1580 |  | 4000 |  | 25 | 0.1 |  | 20 | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Initiated
17 | 053803AAL | Ameren CIPS | 545 N Jordan Dr | Gibson City | Ford | New | Yes | 99020071 | C | 1999-02-19 | 1999-06-16 |  | Permitted | SCT | 2 | Westinghouse | 501D5A |  | No | DLN | 135 | 1457 |  | N.G./Oil | Peaking | 136 (g) 242 (o) | 245 |  |  | 37 |  |  | 25(G),42(O) | 0.10(g)-0.168(o) |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, oper. Hrs | NSPS | Operating
18 | 055803AAB | Entergy -Franklin County Pwr | 2429 Eaton Road | Thompsonville | Franklin | New | Yes | 00080055 | C | 2000-08-22 |  |  | Review Pending | SCT | 2 | GE | 7FA Frame |  | No | DLN | 147.8 | 1747 |  | N. Gas | Peaking |  | 250 | [5 empty] | 9 | 0.036 | [5 empty] | NSPS | Under Review
19 | 055803AAB | Entergy -Franklin County Pwr | 2429 Eaton Road | Thompsonville | Franklin | New | Yes | 00080055 | C | 2000-08-22 |  |  | Review Pending | SCT | 4 | GE | 7EA Frame |  | No | DLN | 72.9 | 787.6 |  | N. Gas | Peaking |  | 250 | [5 empty] | 9 | 0.036 | [5 empty] | NSPS | Under Review
20 | 055807AAD | Gen Power | Woods Road | W.Frankfort | Franklin | New | Yes | 00090005 | C | 2000-09-01 |  |  | Review Pending | SCT | 4 | GE | 7EA Frame |  | No | [5 empty] | Peaking | [14 empty] | PSD Minor | Under Review
21 | 063800AAP | Kinder Morgan-Aux Sable Power Plt | East Route 6 | Morris | Grundy | New | No | 00030031 | C | 2000-03-06 |  |  | Draft Permit | SCT | 4 | GE | LM6000 Aero |  | No | WI | 44 | 403 |  | N.Gas | Peaking | 40 | 247.5 | [5 empty] | 25 | 0.1 |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Under Review
22 | 077806AAA | Ameren CIPs | 1820 Power Plant Rd. | Grand Tower | Jackson | Existing | Yes | 99080101 | C | 1999-08-30 | 2000-02-25 |  | Permitted | CCT | 2 | Westinghouse | 501F |  | Yes | CT (SCR), SCR(HRSG) | 300 | 2050 | 297(1)333(2) | N. Gas Only | Base | 216.8(CT-1) 219.6(CT-2) | 1911.5 | [5 empty] | 40CFR60.44a(d)(1) |  |  |  | Yes | Yes | fuel use,Btu, reagent use, oper. Hrs | NSPS | Const. Initiated
23 | 089425AAC | DMG (Dynegy/Rocky Road) | 1221 Power Dr | E.Dundee | Kane | New | No | 98120016 | C | 1998-12-04 | 2000-06-05 |  | Permitted | SCT | 1 | GE | LM5000 |  | No | WI | 35 | 367 |  | N. Gas Only | Peaking | 60 | 245 |  | 6600 |  |  |  | 25(G),42(O) | 0.10(g)-0.168(o) |  |  | If 3 yr. avg. C.F.>10% | fuel usage | Fuel usage, operating hours, Fuel Btu | NSPS | Operating
24 | 089425AAC | DMG (Dynegy/Rocky Road) | 1221 Power Dr | E.Dundee | Kane | New | No | 98120016 | C | 1998-12-04 | 2000-06-05 |  | Permitted | SCT | 2 | Westinghouse | 501DA |  | No | DLN | 121 | 1439 |  | N. Gas Only | Peaking | 80 | 245 |  | 6600 |  |  |  | 25(G),42(O) | 0.1 (G) |  |  | If 3 yr. avg. C.F.>10% | fuel usage | Fuel usage, operating hours, Fuel Btu | NSPS | Operating
25 | 089425AAC | DMG (Dynegy/Rocky Road) | 1221 Power Dr | E.Dundee | Kane | New | No | 99050098 | C | 1999-05-28 | 1999-10-27 |  | Permitted | SCT | 1 | Westinghouse | 501D5A |  | No | DLN | 121 | 1439 |  | N. Gas Only | Peaking | 80 | 245 |  | 6600 |  |  |  | 25(G),42(O) | 0.1 (G) |  | 20 | If 3 yr. avg. C.F.>10% | fuel usage | Fuel usage, operating hours, Fuel Btu | NSPS | Operating
26 | 089802AAF | Fox River Pkng Stn/Coastal Power Co. | Lasher and Dauberman | Big Rock | Kane | New | No | 99110073 | C | 1999-11-19 |  |  | Final Review | SCT | 3 | ABB | 11N2 Frame |  | No | DLN | 115 | 1362 |  | N.Gas | Peaking | [7 empty] | 25 | 0.1 | [5 empty] | NSPS | Under Review
27 | 091015AAD | Indeck-Bourbonnais Energy Center | East of I57 on George Road | Bourbonnais | Kankakee | New | Yes | 00060010 | C | 2000-06-06 |  |  | No Action | SCT | 4 | GE | 7FA Frame |  | No | DLN | 170.8 | 1540 |  | N.Gas | Peaking | [7 empty] | 9 | 0.036 | [5 empty] | NSPS | Under Review
28 | 091806AAM | Duke Energy | Township Rd 6000 N | Manteno | Kankakee | New | Yes | 00040067 | C | 2000-04-10 |  |  | Public Notice | CCT | 2 | GE | 7FA Frame |  | No | SCR | 310 | 4232 |  | N.Gas | Base | 31.6 | [6 empty] | 3.5 | 0.014 |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | Major | Under Review
29 | 093801AAN | Kendall New Cent. Dev./Enron | Corneils Rd Between Eldermaun and Beeche | Plano | Kendall | New | Yes | 99020032 | C | 1999-02-03 | 2000-01-14 |  | Permitted | SCT | 8 | GE | 7EA Frame |  | No | DLN | 83 | 1002 |  | N. Gas | Peaking | 60 | 426.4 |  |  |  | 3300 | 26400 | 9(yrly),12(monthly)15 (hrly) | 0.037(annual), 0.048(monthly if operated >250 hours/month), 0.060 (hourly) |  |  | If 3 yr. avg. C.F.>10% | Yes | Fuel usage, operating hours, Fuel Btu | PSD/BACT | Const. Pending
30 | 093808AAD | L S Power/Kendall Energy | County Line and Wildy Rds. | Minooka | Kendall | New | No | 98110017 | C | 1998-11-05 | 1999-06-02 |  | Permitted | CCT/SCT* | 4 | GE or Equivalent | 7241 |  | No | CT(DLN), SCR (HRSG)*¹ | 250 | 2166 | 350 | N. Gas Only | Base/Peaking | 188.7 (SCT) 36 (CCT) | 99 (SCT), 630.7 (CCT) |  |  |  | 1048 (SCT) |  | 25 (SCT), 4.5 -G(SCR) | 0.0166(CCT), 0.0936 (SCT) |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/BACT | Const. Pending
31 | 097190AAC | Midwest Generation | 401 E Greenwood Ave | Waukegan | Lake | Existing | No | 95090043 | Title V | 1995-09-07 |  |  | Consoldation | SCT | 4 | Worthington | GG4 |  | Yes | None | 33 | 558 |  | JP-4, N.G. | Peaking |  | No Limit | [5 empty] | 110(JP-4) 70 (g) | 0.44 (o) 0.28(g) | [5 empty] | None | Existing Peaker
32 | 097190AAC | Midwest Generation | 401 E Greenwood Ave | Waukegan | Lake | Existing | No | 00050071 | C | 2000-05-22 |  |  | Review Pending | SCT | 2 | GE | 7FA Frame |  | No | DLN | 145.8 | 1951 |  | N.Gas | Peaking | [7 empty] | 9 | 0.036 | [5 empty] | NSPS | Under Review
33 | 097200ABB | Skygen/Zion Energy Center LLC | West Ninth St | Zion | Lake | New | No | 99110042 | C | 1999-11-12 |  |  | Final Review | SCT | 5 | GE | 7FA Frame |  | No | DLN/WI | 160 | 1719 |  | N.Gas/Oil (back-up) | Peaking | 81(g) 321 (o) | 697.5 |  |  |  | 2300(500-oil) | 11500 | 9(yrly),12(monthly)15 (hrly) | 0.058(hourly) |  |  |  | Yes | Fuel usage, operating hours, Fuel N, Btu | PSD/BACT/NSPS | Under Review
34 | 097810AAC | Carlton Inc./North Shore Power | N. Of 9th St, E Of Union Pacific RR | Zion | Lake | New | No | 99120057 | C | 1999-12-21 |  |  | Final Review | SCT | 3 | GE/ABB | 7FA/11N2 Frame | 6 GE Type EA each 80 MW | No | DLN | 187 | 1746 |  | N.Gas | Peaking | 100.9(7FA); 54.1(7EA) | 245 |  | 8313, Alt. 6888 |  |  |  | 15 | 0.056 |  |  | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | Fuel consumption, Total hrs of operation | NSPS | Under Review
35 | 103814AAC | Lee Cty Gen. Facility/L S Power | Nelson Rd At I-88 | Nelson | Lee | New | Yes | 98080039 | C | 1998-08-11 | 2000-01-28 |  | Permitted | CCT/SCT* | 4 | GE or Equivalent | TBD |  | No | DLN(g)/WI(o),HRSG(SCR)*¹ | 250 | 2516 |  | N.Gas/Oil | Base/Peaking | 36(g) 139(o) | 630.8 |  |  |  | 2000 as SCT | 2453 (g) 96(o) | SCT-25(g),42(o),CCT- 4.5(g)(SCR) |  |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/NSPS | Const. Pending
36 | 103817AAH | Lee Generating Stn./Duke Energy | Nachusa Rd | South Dixon | Lee | New | Yes | 99090029 | C | 1999-09-13 | 2000-03-31 |  | Permitted | SCT | 8 | GE | 7EA Frame |  | No | DLN | 83 | 978 |  | N.Gas/Oil | Peaking | [7 empty] | 12 | 0.0545 | [5 empty] | PSD/BACT | Const. Pending
37 | 107815AAC | Spectrum Energy-Logan County | 1 1/2 Miles E Of New Holland | Sheridan | Logan | New | Yes | 00050025 | C | 2000-05-05 | 2000-09-12 |  | Permitted | SCT | 6 | GE | LM6000 Aero |  | No | WI | 45 | 420 |  | N.Gas | Peaking | [7 empty] | 25 | 0.1 |  |  | Yes | Yes |  | NSPS | Const. Pending
38 | 111805AAP | Reliant Energy | 4500 S Route 47 | Woodstock | McHenry | New | No | 99050089 | C | 1999-05-26 | 1999-12-09 |  | Permitted | SCT | 3 | GE | 7FA Frame |  | No | DLN | 170 | 1874 |  | N.Gas | Peaking | 105 | 248 | 14500 | 14500 |  |  |  | 9 | 0.036 |  |  | Yes | Yes | Fuel usage | PSD/BACT | Const. Pending
39 | 119090AAH | Reliant Energy (Cardinal Energy) | Madison St. East of Hwy 111 | Roxana | Madison | New | No | 98090064 | C | 1998-09-21 | 1999-07-14 |  | Permitted | CCT | 3 | GE/Westinghouse | 7FA/501D |  | No | DLN, SCR (CT, HRSG) | 211 | 1916 | 489 | N.Gas, Refinery Gas | Base | 31.7(w/DB) 25.3(w/o DB) | 330.5 | [5 empty] | 3.5 (8 hr) 4.5(1 hr) | 0.013 |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/BACT | Const. Pending
40 | 119105AAA | Ameren CIPS | 701 Main & McKinley Bridge | Venice | Madison | Existing | No | 95090017 | Title V |  |  |  | Permitted | SCT | 1 | Westinghouse | W-301G |  | Yes | None | 37 | 372 |  | Oil | Peaking | No Limit | No Limit |  |  | No Limit | No Limit | No Limit | 110 | 0.44 |  |  | No | No |  | None | Operating
41 | 121803AAA | Ameren Energy Gen. Company-Kinmundy | 2816 Kinoka Rd | Patoka | Marion | New | Yes | 99020027 | C | 1999-02-04 | 1999-06-28 |  | Permitted | SCT | 2 | Westinghouse | 501D5A |  | No | DLN(g),WI(o) | 135 | 1457 |  | N.G./Dis. Oil | Peaking | 136(g) 242(o) | 245 |  |  | 37 |  |  | 25(G),42(O) | 0.1 (G) |  |  | Yes | Yes | fuel use,Btu,N, water/fuel, oper. Hrs | NSPS | Const. Initiated
42 | 127899AAA | Electric Energy/Midwest Elec. Power | 2100 Portland Rd | Joppa | Massac | Existing | Yes | 99100060 | C | 2000-06-23 | 2000-07-25 |  | Permitted | SCT | 3 | GE | Frame 7B |  | No | WI | 72 | 743 |  | N.Gas | Peaking | 89.5 | 349.3 |  | 4032 |  |  |  | 40 | 0.16 | [5 empty] | Netted | Operating
43 | 127899AAA | Electric Energy/Midwest Elec. Power | 2100 Portland Rd | Joppa | Massac | Existing | Yes | 99100060 | C | 2000-06-23 | 2000-07-25 |  | Permitted | SCT | 2 | GE | Frame 7B |  | No | WI | 51 |  |  | N.Gas | Peaking |  |  |  | 4032 | [10 empty] | Netted | Operating
44 | 145842AAA | Ameren Energy Gen. Company | 4646 White Walnut Rd | Pinckneyville | Perry | New | Yes | 99090035 | C | 1999-09-13 | 1999-11-09 |  | Permitted | SCT | 8 | GE/Stewart & Stevenson | LM6000 Aero |  | No | WI | 48.5 | 444 |  | N.Gas | Peaking | 57 | [6 empty] | 35 | 0.14 | [5 empty] | NSPS | Operating
45 | 145842AAA | Ameren Energy Gen. Company | 4646 White Walnut Rd | Pinckneyville | Perry | New | Yes | 00090076 | C | 2000-09-28 |  |  | Review Pending | SCT | 4 | GE | PG6581 |  | No | DLN | 48 | 553 |  | N.Gas | Peaking | [14 empty] | NSPS | Under Review
46 | 147803AAA | MEP Investments-Deland | To Be Announced | Goose Creek | Piatt | New | Yes | 00090082 | C | 2000-09-28 |  |  | Review Pending |  | 6 | GE | 7EA Frame |  | No | DLN | 94.5 |  |  | N.Gas | Peaking | [14 empty] | NSPS | Under Review
47 | 161807AAN | Cordova Energy | SW Corner 192nd St.,and 250th St. | Cordova | Rock Island | New | Yes | 99020097 | C | 1999-02-26 | 1999-09-02 |  | Permitted | CCT | 2 |  |  |  | No | DLN (g), SCR (HRSG) | 250 | 1974 |  | N.Gas | Base | 35 | 306.6 | [5 empty] | 4.5 | 0.019 |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/BACT | Const. Pending
48 | 167822ABG | CWLP | 3620 Ridgely Rd | Springfield | Sangamon | New | Yes | 94120058 | O | 1997-03-14 | 1997-03-21 | 2002-03-14 | Permitted | SCT | 1 | Westinghouse | 501D5A |  | No | WI | 100 | 1370 |  | N.G./#2 Oil | Peaking | 750 | 249 | [5 empty] | 75(G),75(O) | 0.3 |  |  | Yes |  | fuel usage,Btu, water usage, oper. Hrs | NSPS | Operating
49 | 171851AAA | Soyland Power | 1175 E Campbell Rd | Alsey | Scott | New | Yes | 98120050 | C | 1998-12-06 | 1999-03-24 |  | Permitted | SCT | 2 | Westinghouse | 251AA Frame |  | No | DLN | 30 | 375 |  | N.Gas/Oil | Peaking | [7 empty] | About 175 | 0.7 | [5 empty] | old unit | Operating
50 | 171851AAA | Soyland Power | 1175 E Campbell Rd | Alsey | Scott | New | Yes | 98120050 | C | 1999-12-09 | 2000-07-02 |  | Permitted | SCT | 1 | Westinghouse | 251AA Frame |  | No | WI | 25 | 341 |  | N.Gas/Oil | Peaking | [7 empty] | 148 | 0.59 | [5 empty] | old unit | Under Review
51 | 173801AAA | Shelby Enrgy Cntr/ Reliant Energy | Us 45 @ County Rd 35 | Sigel | Shelby | New | Yes | 99090085 | C | 1999-09-30 | 2000-02-23 |  | Permitted | SCT | 8 | GE | LM6000 Aero |  | No | WI | 41 | 444 |  | N.Gas Only | Peaking | 40 | 198 |  | 4186 |  |  |  | 25 | 0.09 |  |  | Yes | Yes | Fuel usage, operating hours, Fuel Btu | NSPS | Operating
52 | 173807AAG | Holland Energy, LLC | RR2, County Line Rd. | Holland | Shelby | New | Yes | 99100022 | C | 1999-10-07 | 2000-04-05 |  | Permitted | CCT | 2 |  |  |  | No | DLN(g),WI(o),SCR(HRSG) | 168 | 1762 | 776 | NG/Oil (CT), NG(D.B.) | Base | 41.7 | 342 |  |  |  | DB<1500, o<1000 |  | 4.5(hrly) 3.5(24 hr);16 (o)(hrly) | 0.02(g),0.04(o) |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/BACT | Const. Initiated
53 | 183090AAE | DMG/Tilton Energy Center | 80 W First St | Tilton | Vermilion | New | Yes | 98110018 | O | 1999-10-22 | 2000-06-01 | 2002-04-01 | Permitted | SCT | 4 | GE | LM6000 Aero |  | No | WI | 44 | 410 |  | N.Gas Only | Peaking | 50 | 197 |  | 4250 |  |  |  | 25 | 0.1 | [5 empty] | NSPS | Operating
54 | 189802AAA | MEP Investments-Posen | To Be Announced | Bolo | Washington | New | Yes | 00090081 | C | 2000-09-28 |  |  | Review Pending | SCT | 6 | GE | 7EA Frame |  | No | DLN | 94.5 |  |  | N.Gas | Peaking | [14 empty] | NSPS | Under Review
55 | 197030AAO | Power Energy Partners/Crete Energy Park | Burville Road Access | Crete | Will | New | No | 99120056 | C | 1999-12-20 |  |  | Draft Permit | SCT | 3 | ABB | 11N2 Frame | Equivalent to GE11N2 | No | DLN or WI | 131 | 1624 |  | N.Gas | Peaking | 125.47 | 245 |  | 6040 |  |  |  | 25 | 0.07 | 20% higher than normal emissions | Explain if >20 min. | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | Fuel usage, operating hours, Fuel Btu | NSPS | Under Review
56 | 197035AAG | Elwood Energy/Peoples Gas | 20900 West Noel Road | Elwood | Will | New | No | 00010076 | C | 2000-01-27 | 2000-10-17 |  | Permitted | SCT | 2 | GE | 7FA Frame |  | No | DLN | 172 | 1763 |  | N.Gas | Peaking | 64.8 | 217.56 |  |  |  | 3200 |  | 9 | 0.037 |  |  | Yes | Fuel usage | Fuel usage, operating hours, Fuel Btu | Major-PSD | Const. Pending
57 | 197035AAH | Elwood Energy/Peoples Gas | 20900 West Noel Road | Elwood | Will | New | No | 00010077 | C | 2000-01-27 | 2000-10-17 |  | Permitted | SCT | 3 | GE | 7FA Frame |  | No | DLN | 172 | 1763 |  | N.Gas | Peaking | 64.8 | 326.34 |  |  |  | 3200 |  | 9 | 0.037 |  |  | Yes | Fuel usage | Fuel usage, operating hours, Fuel Btu | Major-PSD | Const. Pending
58 | 197808AAG | Elwood Energy Center,LLC | 21100 W Noel Rd | Elwood | Will | New | No | 98060091 | C | 1999-02-18 | 2000-10-17 |  | Permitted | SCT | 4 | GE | 7FA Frame |  | No | DLN | 170 | 1763 |  | N.G./Ethane | Peaking | 108 | 1565.7 |  |  |  | Peaking Use Only |  | 15 | 0.061 |  |  | Yes | Yes | fuel usage, Btu, fuel N, oper. Hrs | PSD/BACT | Operating
59 | 197808AAG | Elwood Energy Center,LLC | 21100 W Noel Rd | Elwood | Will | New | No | 98060091 | C | 1999-04-02 | 2000-10-17 |  | Permitted | CCT | 10 | GE | 7FA Frame |  | No | DLN,SCR | 250 | 1763 | ?? | N.G./Ethane | Base | 32.4 | 1565.7 |  |  |  | 6000 |  | 4.5 | 0.0184 |  |  | Yes | Yes | fuel use,Btu,N, reagent use, oper. Hrs | PSD/BACT | Const. Pending
60 | 197810ABS | Rolls-Royce/Lockport Pwr Gen. | East Of I and M Canal | Lockport | Will | New | No | 00050010 | C | 2000-05-01 | 2000-10-27 |  | Permitted | SCT | 6 | RR | Trent(p) Aero |  | No | DLN | 62 | 492 |  | N.Gas | Peaking |  | 245 | [5 empty] | 25 | 0.1 |  | Yes |  | Yes |  | NSPS | Under Review
61 | 197811AAH | Desplaines Greenland/Enron | 27155 S Kankakee St | Manhattan | Will | New | No | 99020021 | C | 1999-02-03 | 1999-09-28 |  | Permitted | SCT | 8 | GE | 7EA Frame |  | No | DLN | 83 | 1002 |  | N.Gas | Peaking |  | 419.4 |  |  |  | 3250 |  | 9(yrly),12(monthly)15 (hrly) | 0.037(annual), 0.048(monthly if oper'd >250 hrs/m),0.060 (hourly) |  |  | Yes |  | Fuel usage, operating hours, Fuel Btu | PSD/BACT | Operating
62 | 197811AAH | Desplaines Greenland/Enron | 27155 S Kankakee St | Manhattan | Will | New | No | 99020021 | C | 2000-04-03 |  |  | Final Revision | SCT | 1 | GE | 7FA Frame |  | No | DLN | 167 | 2750 ?? |  | N.Gas | Peaking | [5 empty] | 3250 | [5 empty] | Yes |  | Fuel usage, operating hours, Fuel Btu | PSD/BACT | Under Review
63 | 197899AAB | Univ. Park Energy/ Constellation Po. | SW Intersection Of Central Ave and Dralle Rd | Univ. Park | Will | New | No | 99120020 | C | 1999-12-06 | 2000-05-01 |  | Permitted | Aero CT | 6 | Pratt & Whittney | FT8 "Twin Packs" Aero |  | No | WI | 50 | 494 |  | N.Gas | Peaking | 30 | 245 |  | 4443 |  |  |  | 25 | 0.1 |  | Explanation if >20 minutes | If 3 yr. avg. C.F.>10% | fuel usage, water/fuel ratio, | fuel usage,Btu, water usage, oper. Hrs | NSPS | Const. Initiated
64 | 197899AAC | Univ. Park Power (PPL Global) | Dralle Road | Univ. Park | Will | New | No | 00080078 | C | 2000-08-17 |  |  | Review Pending | SCT | 12 | GE | LM6000PC |  | No | WI+SCR | 44.2 | 452 |  | N. Gas | Peaking | [7 empty] | 25 (WI) 5(WI+SCR) | 0.1(scr) 0.02(WI+SCR) | [5 empty] | NSPS | Under Review
65 | 199856AAC | Southern Ill. Power Coop. | 11543 Lake Of Egypt Rd | Marion | Williamson | Existing | Yes | 00070029 | C | 2000-07-12 |  |  | Draft Permit | SCT | 2 | GE | PG7172 (EA) |  | No | DLN | 83 | 1165 |  | N.Gas/Oil | Peaking | [7 empty] | 15(g),42 (o) | 0.06(g).17 (o) | [5 empty] | Netting | Under Review
66 | 199856AAK | Reliant Energy/ Williamson Enrgy Cntr | Hwy 13 Near Hwy 166 | Crab Orchard | Williamson | New | Yes | 99090084 | C | 1999-09-30 | 1999-12-20 |  | Permitted | SCT | 8 | GE | LM6000 Aero |  | No | WI | 41 | 444 |  | N.Gas | Peaking | 40 | 198 |  | 4186 |  |  |  | 25 | 0.1 |  |  | Yes | Yes | Fuel usage, operating hours, Fuel Btu | NSPS | Const. Pending
67 | 201030BCG | Indeck-Rockford | 136 Harrison Ave | Rockford | Winnebago | New | Yes | 99110088 | C | 1999-11-24 | 2000-02-16 |  | Permitted | SCT | 2 | SW | V84 Frame |  | No | DLN | 150 | 1698.5 |  | N.Gas | Peaking |  | 199 | [5 empty] | 15 | 0.06 | [5 empty] | NSPS | Operating
|  | Total | [12 empty] | 279 | [5 empty] | 7948 | 77659.6 |  |  |  |  | 16311.6
Abbreviations: DLN=Dry Low NOx burner, WI= Water Injection, SCR=Selective Catalytic Reduction, SCN= Sconox, CT=Combution Turbine, SCT= Simple Combustion Turbine, CCT= Combined Cycle Turbine,
HRSG= Heat Recovery Steam Generator, EGU= Electric Generating Unit, C= Construction, O=Operating, MW=Megawatt, NG=Natural Gas, F.Oil=Fuel Oil, tpy=tons/year, JP-4=Jet Fuel, D.B.=Duct Burner, G=Gas, O=Oil
*SCT or CCT . The company has not made the final decision
** Currently many new EGUs are operating under the construction permit, and they are planning to apply for Title V permit. Title V permit has been applied for existing Waukegan and Fisk peakers
*** Combined Cycle may be chosen in place of single cycle turbines
*¹ DLN when n.gas used, WI when oil is fired, HRSG s controlled by SCR |  |  |  | *³ 99 ppm NOx is approximately equal to 0.397 lb/mmBtu for gas turbines burning natural gas as per ACT for Turbines
*² 40 CFR75 monitoring required if 3-year annual average capacity factor exceeds 10% and, if oil is also fired, and average annual heat input from oil exceeds 15%.